## Intellus Registers
Address | Representation | Word Size | ClassID | MemberId | Instance | Enum Values
100 | eREPRESENTATION_UWORD | 1 | eWATBUS_CLASS_REAL_TIME_CLOCK | eREAL_TIME_MEMBER_YEAR | 1
101 | eREPRESENTATION_UBYTE | 1 | eWATBUS_CLASS_REAL_TIME_CLOCK | eREAL_TIME_MEMBER_MONTH | 1
102 | eREPRESENTATION_UBYTE | 1 | eWATBUS_CLASS_REAL_TIME_CLOCK | eREAL_TIME_MEMBER_DAY | 1
103 | eREPRESENTATION_UBYTE | 1 | eWATBUS_CLASS_REAL_TIME_CLOCK | eREAL_TIME_MEMBER_HOUR | 1
104 | eREPRESENTATION_UBYTE | 1 | eWATBUS_CLASS_REAL_TIME_CLOCK | eREAL_TIME_MEMBER_MINUTE | 1
105 | eREPRESENTATION_UBYTE | 1 | eWATBUS_CLASS_REAL_TIME_CLOCK | eREAL_TIME_MEMBER_SECONDS | 1
300 | eREPRESENTATION_STRING | 1 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_ACTIVE_PROGRAM | 1
301 | eREPRESENTATION_STRING | 4 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_RUNNING_NAME_LEFT | 1
305 | eREPRESENTATION_STRING | 4 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_RUNNING_NAME_RIGHT | 1
309 | eREPRESENTATION_UWORD | 1 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_RUNNING_PROGRAM_STEP | 1
310 | eREPRESENTATION_UWORD | 1 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_RUNNING_SEQUENCE_STEP | 1
311 | eREPRESENTATION_UWORD | 1 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_RUNNING_SEQUENCE_ITER | 1
312 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_DLI_DAILY_LIGHT_INTEGRAL | 1
314 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_PERCIVAL_PROGRAM | ePERCIVAL_PROGRAM_MEMBER_DLI_ACCRUED | 1
500 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 1
502 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 2
504 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 3
506 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 4
508 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 5
510 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 6
512 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ANALOG_IN | eANALOG_IN_MEMBER_PROCESS_VALUE | 7
700 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 1
702 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 2
704 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 3
706 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 4
708 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 5
710 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 6
712 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_SET_POINT_ACTIVE_CLOSED | 7
714 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_HEAT_OUTPUT | 2 | 59 = NO, 106 = YES
715 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_COOL_OUTPUT | 2 | 59 = NO, 106 = YES
716 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_HEAT_OUTPUT | 3 | 59 = NO, 106 = YES
717 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_COOL_OUTPUT | 3 | 59 = NO, 106 = YES
718 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_HEAT_OUTPUT | 4 | 59 = NO, 106 = YES
719 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_COOL_OUTPUT | 4 | 59 = NO, 106 = YES
720 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_HEAT_OUTPUT | 5 | 59 = NO, 106 = YES
721 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_COOL_OUTPUT | 5 | 59 = NO, 106 = YES
722 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_HEAT_OUTPUT | 6 | 59 = NO, 106 = YES
723 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_COOL_OUTPUT | 6 | 59 = NO, 106 = YES
724 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_HEAT_OUTPUT | 7 | 59 = NO, 106 = YES
725 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_CONTROL_LOOP_2 | eCONTROL_LOOP_2_MEMBER_ENABLE_COOL_OUTPUT | 7 | 59 = NO, 106 = YES
900 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 1
901 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 1
903 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 2 | 63d = ON, 62d = OFF
904 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 2
906 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 3 | 63d = ON, 62d = OFF
907 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 3
909 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 4 | 63d = ON, 62d = OFF
910 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 4
912 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 5 | 63d = ON, 62d = OFF
913 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 5
915 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 6 | 63d = ON, 62d = OFF
916 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 6
918 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 7 | 63d = ON, 62d = OFF
919 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 7
921 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 8 | 63d = ON, 62d = OFF
922 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 8
924 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 9 | 63d = ON, 62d = OFF
925 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 9
927 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 10 | 63d = ON, 62d = OFF
928 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 10
930 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 11 | 63d = ON, 62d = OFF
931 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 11
933 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 12 | 63d = ON, 62d = OFF
934 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 12
936 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 13 | 63d = ON, 62d = OFF
937 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 13
939 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 14 | 63d = ON, 62d = OFF
940 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 14
942 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 15 | 63d = ON, 62d = OFF
943 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 15
945 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 16 | 63d = ON, 62d = OFF
946 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 16
948 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 17 | 63d = ON, 62d = OFF
949 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 17
951 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 18 | 63d = ON, 62d = OFF
952 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 18
954 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 19 | 63d = ON, 62d = OFF
955 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 19
957 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 20 | 63d = ON, 62d = OFF
958 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 20
960 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 21 | 63d = ON, 62d = OFF
961 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 21
963 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 22 | 63d = ON, 62d = OFF
964 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 22
966 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 23 | 63d = ON, 62d = OFF
967 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 23
969 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 24 | 63d = ON, 62d = OFF
970 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 24
972 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 25 | 63d = ON, 62d = OFF
973 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 25
975 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 26 | 63d = ON, 62d = OFF
976 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 26
978 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 27 | 63d = ON, 62d = OFF
979 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 27
981 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 28 | 63d = ON, 62d = OFF
982 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 28
984 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 29 | 63d = ON, 62d = OFF
985 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 29
987 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 30 | 63d = ON, 62d = OFF
988 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 30
990 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 31 | 63d = ON, 62d = OFF
991 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 31
993 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 32 | 63d = ON, 62d = OFF
994 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 32
996 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 33 | 63d = ON, 62d = OFF
997 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 33
999 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 34 | 63d = ON, 62d = OFF
1000 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 34
1002 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 35 | 63d = ON, 62d = OFF
1003 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 35
1005 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 36 | 63d = ON, 62d = OFF
1006 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 36
1008 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 37 | 63d = ON, 62d = OFF
1009 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 37
1011 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 38 | 63d = ON, 62d = OFF
1012 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 38
1014 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 39 | 63d = ON, 62d = OFF
1015 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 39
1017 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 40 | 63d = ON, 62d = OFF
1018 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 40
1020 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 41 | 63d = ON, 62d = OFF
1021 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 41
1023 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 42 | 63d = ON, 62d = OFF
1024 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 42
1026 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 43 | 63d = ON, 62d = OFF
1027 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 43
1029 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 44 | 63d = ON, 62d = OFF
1030 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 44
1032 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 45 | 63d = ON, 62d = OFF
1033 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 45
1035 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 46 | 63d = ON, 62d = OFF
1036 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 46
1038 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_STATE | 47 | 63d = ON, 62d = OFF
1039 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_POWER | 47
1041 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 1
1043 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 2
1045 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 3
1047 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 4
1049 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 5
1051 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 6
1053 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 7
1055 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 8
1057 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 9
1059 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 10
1061 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 11
1063 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 12
1065 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 13
1067 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 14
1069 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 15
1071 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 16
1073 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 17
1075 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 18
1077 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 19
1079 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 20
1081 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 21
1083 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 22
1085 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 23
1087 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 24
1089 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 25
1091 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 26
1093 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 27
1095 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 28
1097 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 29
1099 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 30
1101 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 31
1103 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 32
1105 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 33
1107 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 34
1109 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 35
1111 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 36
1113 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 37
1115 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 38
1117 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 39
1119 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 40
1121 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 41
1123 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 42
1125 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 43
1127 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 44
1129 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 45
1131 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 46
1133 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DIGITAL_IO | eDIGITAL_IO_MEMBER_LIGHT_ON_TIME | 47
1150 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_PERCIVAL_DEFROST | ePERCIVAL_DEFROST_MEMBER_ACTIVE | 1
1300 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_LIMIT_1+1) |  | 59 = NO, 106 = YES
1302 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_LIMIT_1+1)
1304 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_1+1)
1306 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_1+1)
1308 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_1_DEVIATION+1)
1310 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_1_DEVIATION+1)
1312 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_2+1)
1314 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_2+1)
1316 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_3+1)
1318 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_3+1)
1320 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_4+1)
1322 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_4+1)
1324 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_5+1)
1326 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_5+1)
1328 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_6+1)
1330 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_6+1)
1332 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_HIGH_SETPOINT | (eALARM_AIN_PV_7+1)
1334 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LOW_SETPOINT | (eALARM_AIN_PV_7+1)
1336 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_LIMIT_1+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1337 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_1_DEVIATION+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1338 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_1+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1339 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_2+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1340 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_3+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1341 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_4+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1342 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_5+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1343 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_6+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1344 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_STATE | (eALARM_AIN_PV_7+1) |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR
1345 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_ALARM_2 | eALARM_2_MEMBER_LIGHT_LIFE_ALARM_STATUS | 1 |  | 63d = ON, 62d = OFF, 108 = ON w/ACK
1500 | eREPRESENTATION_ULONG | 2 | eWATBUS_CLASS_DEVICE | eDEVICE_MEMBER_LIGHT_LIFE_ALARM | 1
1700 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_PERCIVAL_OVERTEMPERATURE | ePERCIVAL_OT_MEMBER_SETPOINT_HIGH | 1
1702 | eREPRESENTATION_FLOAT | 2 | eWATBUS_CLASS_PERCIVAL_OVERTEMPERATURE | ePERCIVAL_OT_MEMBER_SETPOINT_LOW | 1
1704 | eREPRESENTATION_WIDE_ENUM | 1 | eWATBUS_CLASS_PERCIVAL_OVERTEMPERATURE | ePERCIVAL_OT_MEMBER_ALARM_STATE | 1 |  | 88d = START, 61d = NONE, 12d = BLOCKED, 8d = ALARM LOW, 7d = ALARM HIGH, 28d = ERROR

## hex to floating point
This sheet requires the Analysis Toolpak to be loaded. Select the Tools Menu > Add-Ins... > check Analysis Toolpack
|  | most significant |  |  | Least significant
|  | high word |  | low word |  | INSTRUCTIONS
2 words | decimal | 16457 |  | 4059 |  | < Enter these 2 words as decimal numbers
| hex | 4049 |  | 0FDB |  | < or enter these 2 words in hex
|  | high byte |  |  | low byte
4 bytes | decimal | 64 | 73 | 15 | 219 | < or enter these 4 bytes as decimal numbers
| hex | 40 | 49 | 0F | DB | < or enter these 4 bytes in hex
32 bits | binary | 01000000 | 01001001 | 00001111 | 11011011 | < or enter these 4 bytes as 8 bit binary strings
[6 empty] | alternate method of calculating the mantissa |  |  | if No Exponent bits
for numbers near zero
positive numbers less than 1E-38 (numbers starting with less than 00 7F)
| first bit | 0 |  |  |  |  | each row is half of that above |  | negative numbers greater than -1E-38 (numbers starting with less than 10 7F)
| invert | 1 | SIGN |  |  |  | 1 | 1 | 1
[5 empty] | final 23 bits | 1 | 0.5 | 0.5 | 0
| next 8 bits | 10000000 |  |  |  | 0 | 0.25 | 0 | 0
| decimal | 128 |  |  |  | 0 | 0.125 | 0 | 0.125
| subtract 127 | 1 | EXPONENT |  |  | 1 | 0.0625 | 0.0625 | 0
[6 empty] | 0 | 0.03125 | 0 | 0
| final 23 bits | 10010010000111111011011 |  |  |  | 0 | 0.015625 | 0 | 0.015625
|  |  | if no exponent bits |  |  | 1 | 0.0078125 | 0.0078125 | 0
| decimal | 4788187 | 4788187 |  |  | 0 | 0.0039062 | 0 | 0
| 80 00 00 hex | 8388608 | 4194304 | 40 00 00 hex |  | 0 | 0.0019531 | 0 | 0
| divide above and add 1 | 1.5708 | 1.1416 | divide above |  | 0 | 0.00097656 | 0 | 0
|  | 1.5708 | MANTISSA ( SIGNIFICAND ) |  |  | 0 | 0.00048828 | 0 | 0.00048828
[6 empty] | 1 | 0.00024414 | 0.00024414 | 0.00024414
| FLOAT = SIGN x MANTISSA x ( 2 ^ EXPONENT ) |  |  |  |  | 1 | 0.00012207 | 0.00012207 | 0.00012207
[6 empty] | 1 | 6.1035e-05 | 6.1035e-05 | 6.1035e-05
| FLOAT | 3.1416 |  |  |  | 1 | 3.0518e-05 | 3.0518e-05 | 3.0518e-05
[6 empty] | 1 | 1.5259e-05 | 1.5259e-05 | 1.5259e-05
Courtesy of | [5 empty] | 1 | 7.6294e-06 | 7.6294e-06 | 0
[6 empty] | 0 | 3.8147e-06 | 0 | 3.8147e-06
[6 empty] | 1 | 1.9073e-06 | 1.9073e-06 | 1.9073e-06
[6 empty] | 1 | 9.5367e-07 | 9.5367e-07 | 0
[6 empty] | 0 | 4.7684e-07 | 0 | 4.7684e-07
[6 empty] | 1 | 2.3842e-07 | 2.3842e-07 | 2.3842e-07
www.simplymodbus.ca | [5 empty] | 1 | 1.1921e-07 | 1.1921e-07
Rev03 - Sep 4, 2013 | [6 empty] | total | 1.5708 | 1.1416
[7 empty] | total | 1.5708 | MANTISSA ( SIGNIFICAND )

## floating point to hex
This sheet requires the Analysis Toolpak to be loaded. Select the Tools Menu > Add-Ins... > check Analysis Toolpack
| FLOAT | 3.1416 | < Enter floating point number |  |  | Courtesy of
FLOAT = SIGN x MANTISSA x ( 2 ^ EXPONENT )
|  | 1 | SIGN
| 1st bit | 0
www.simplymodbus.ca
|  | 1 | EXPONENT |  |  | Rev03 - Sep 4, 2013
| add 127 | 128
| next 8 bits | 10000000
|  | 1.5708 | MANTISSA ( SIGNIFICAND )
or if no exponent bits
| subtract 1 | 0.5708 |  | 1.5708 | mantissa
| 80 00 00 hex | 8388608 |  | 4194304 | 40 00 00 hex
| multiply | 4788186.6333 |  | 6588397.3167 | multiply
4788186.6333
| div by 256 | 18703.854
| integer | 18703
| remainder | 218.6333
| div by 256 | 73.0586
| integer | 73
| remainder | 15
| final 23 bits |  | 10010010000111111011010
1001001
32 bits | binary | 01000000 | 01001001 | 00001111 | 11011010
4 bytes | hex | 40 | 49 | 0F | DA
| decimal | 64 | 73 | 15 | 218
|  | byte1 | byte2 | byte3 | byte4
|  | high byte |  |  | low byte
2 words | hex | 4049 |  | 0FDA
| decimal | 16457 |  | 4058
|  | high word |  | low word
|  | most significant |  |  | Least significant
|  |  | alternate method of calculating the | final 23 bits
if no exponent bits
for numbers near zero
|  | subtract if result>0 | 1.5708 | "1" id result>0 | 1.5708
|  | 1 | 0.5708 |  | 0.5708 | 1
|  | 0.5 | 0.070796 | 1 | 0.070796 | 1
|  | 0.25 | 0.070796 | 0 | 0.070796 | 0
|  | 0.125 | 0.070796 | 0 | 0.070796 | 0
|  | 0.0625 | 0.0082963 | 1 | 0.0082963 | 1
|  | 0.03125 | 0.0082963 | 0 | 0.0082963 | 0
|  | 0.015625 | 0.0082963 | 0 | 0.0082963 | 0
|  | 0.0078125 | 0.00048383 | 1 | 0.00048383 | 1
|  | 0.0039062 | 0.00048383 | 0 | 0.00048383 | 0
|  | 0.0019531 | 0.00048383 | 0 | 0.00048383 | 0
|  | 0.00097656 | 0.00048383 | 0 | 0.00048383 | 0
|  | 0.00048828 | 0.00048383 | 0 | 0.00048383 | 0
|  | 0.00024414 | 0.00023969 | 1 | 0.00023969 | 1
|  | 0.00012207 | 0.00011762 | 1 | 0.00011762 | 1
|  | 6.1035e-05 | 5.6581e-05 | 1 | 5.6581e-05 | 1
|  | 3.0518e-05 | 2.6063e-05 | 1 | 2.6063e-05 | 1
|  | 1.5259e-05 | 1.0804e-05 | 1 | 1.0804e-05 | 1
|  | 7.6294e-06 | 3.1749e-06 | 1 | 3.1749e-06 | 1
|  | 3.8147e-06 | 3.1749e-06 | 0 | 3.1749e-06 | 0
|  | 1.9073e-06 | 1.2676e-06 | 1 | 1.2676e-06 | 1
|  | 9.5367e-07 | 3.1392e-07 | 1 | 3.1392e-07 | 1
|  | 4.7684e-07 | 3.1392e-07 | 0 | 3.1392e-07 | 0
|  | 2.3842e-07 | 7.5498e-08 | 1 |  | 1
|  | 1.1921e-07 |  | 1

## dictionary
1 | 1 | eWORD_SETUP_AINS | eTEXT_2
2 | 2 | eWORD_SETUP_DINS | eTEXT_3
3 | 3 | eWORD_LOGIC_TYPE | eTEXT_50_HZ
4 | 4 | eWORD_SETUP_OUTPUTS | eTEXT_60_HZ
5 | 5 | eWORD_MONITOR | eTEXT_ACTIVE
6 | 6 | eWORD_ALARM | eTEXT_ALARM
7 | 7 | eWORD_ALARM_HIGH | eTEXT_ALARM_HIGH
8 | 8 | eWORD_ALARM_LOW | eTEXT_ALARM_LOW
9 | 9 | eWORD_AMBIENT_ERROR
10 | A | eWORD_AUTO | eTEXT_AUTO
11 | B | eWORD_SOURCE_EVENT_11 | eTEXT_B
12 | C | eWORD_DIRECT | eTEXT_BLOCKED
13 | D | eWORD_BOTH | eTEXT_BOTH
14 | E | eWORD_BROADCAST | eTEXT_BUMPLESS
15 | F | eWORD_C | eTEXT_C
16 | 10 | eWORD_SETUP_DEFROST | eTEXT_PROFILE_01_STEP_X
17 | 11 | eWORD_FAN_DELAY | eTEXT_CLOSE_ON_ALARM
18 | 12 | eWORD_COMPLETE | eTEXT_COMPLETE
19 | 13 | eWORD_SOURCE_AIN1 | eTEXT_PROFILE_04_STEP_X
20 | 14 | eWORD_COOL
21 | 15 | eWORD_DAY | eTEXT_CRITICAL
22 | 16 | eWORD_NIGHT | eTEXT_CURRENT
23 | 17 | eWORD_SOURCE_EVENT_12 | eTEXT_D
24 | 18 | eWORD_DEVIATION_ALARM | eTEXT_DEVIATION_ALARM
25 | 19 | eWORD_RM_CONFIGURATION | eTEXT_CURRENT_PROCESS
26 | 1A | eWORD_SOURCE_EVENT_13 | eTEXT_E
27 | 1B | eWORD_END
28 | 1C | eWORD_ERROR
29 | 1D | eWORD_EVENT | eTEXT_EVENT
30 | 1E | eWORD_F | eTEXT_F
31 | 1F | eWORD_TIMER | eTEXT_FACTORY
32 | 20 | eWORD_FAIL
33 | 21 | eWORD_FIXED | eTEXT_FIXED
34 | 22 | eWORD_FIXED_TIME_BASE | eTEXT_FIXED_TIME_BASE
35 | 23 | eWORD_DHCP | eTEXT_FLOW
36 | 24 | eWORD_HEAT
37 | 25 | eWORD_HIGH | eTEXT_HIGH
38 | 26 | eWORD_HOME
39 | 27 | eWORD_HOURS
40 | 28 | eWORD_ACTIVE_HIGH | eTEXT_HUNDREDTHS
41 | 29 | eWORD_ACTIVE_LOW | eTEXT_INACTIVE
42 | 2A | eWORD_DALI_LIGHT_DIM | eTEXT_ALARM_SET_POINT_LOW
43 | 2B | eWORD_CHA_AUX | eTEXT_SECURITY_PAGE
44 | 2C | eWORD_INPUT | eTEXT_INPUT_DRY_CONTACT
45 | 2D | eWORD_SOURCE_SP1 | eTEXT_PROFILE_05_STEP_X
46 | 2E | eWORD_SOURCE_EVENT_14 | eTEXT_J
47 | 2F | eWORD_HOLD
48 | 30 | eWORD_SOURCE_EVENT_15 | eTEXT_K
49 | 31 | eWORD_LATCHING
50 | 32 | eWORD_DEFROST_TERMINATE | eTEXT_UNUSED_STEP
51 | 33 | eWORD_DIURNAL_PROGRAM | eTEXT_LIMIT_HIGH
52 | 34 | eWORD_DLI_PROGRAM | eTEXT_LIMIT_LOW
53 | 35 | eWORD_LOW | eTEXT_LOW
54 | 36 | eWORD_MANUAL | eTEXT_MANUAL
55 | 37 | eWORD_SOURCE_AIN2 | eTEXT_PROFILE_06_STEP_X
56 | 38 | eWORD_MILLIVOLTS | eTEXT_MILLIVOLTS
57 | 39 | eWORD_MINUTES
58 | 3A | eWORD_SOURCE_EVENT_16 | eTEXT_N
59 | 3B | eWORD_NO | eTEXT_NO
60 | 3C | eWORD_NON_LATCHING
61 | 3D | eWORD_NONE | eTEXT_NONE
62 | 3E | eWORD_OFF | eTEXT_OFF
63 | 3F | eWORD_ON | eTEXT_ON
64 | 40 | eWORD_ON_OFF | eTEXT_ON_OFF
65 | 41 | eWORD_OPEN
66 | 42 | eWORD_SETUP_DALI_CONFIG | eTEXT_OPEN_ON_ALARM
67 | 43 | eWORD_OSCILLATION
68 | 44 | eWORD_OUTPUT | eTEXT_OUTPUT
69 | 45 | eWORD_OVER
70 | 46 | eWORD_PERCENT
71 | 47 | eWORD_PID | eTEXT_PID
72 | 48 | eWORD_OUTPUT_POWER | eTEXT_CURRENT_SET_POINT
73 | 49 | eWORD_24_HOUR_NON_RAMPING | eTEXT_POWER
74 | 4A | eWORD_24_HOUR_RAMPING | eTEXT_PRESSURE
75 | 4B | eWORD_ELAPSED_NON_RAMPING | eTEXT_PROCESS
76 | 4C | eWORD_ELAPSED_RAMPING | eTEXT_PROCESS_ALARM
77 | 4D | eWORD_PROGRAM | eTEXT_PROFILE
78 | 4E | eWORD_ALARM_SET_POINT_HIGH
79 | 4F | eWORD_DISABLED | eTEXT_START_PROFILE
80 | 50 | eWORD_SOURCE_EVENT_17 | eTEXT_R
81 | 51 | eWORD_RATE
82 | 52 | eWORD_SEQUENCE | eTEXT_RESET_LIMIT
83 | 53 | eWORD_SOURCE_SP2 | eTEXT_PROFILE_07_STEP_X
84 | 54 | eWORD_SOURCE_EVENT_18 | eTEXT_S
85 | 55 | eWORD_DOWN | eTEXT_SET_POINT
86 | 56 | eWORD_10_MPS | eTEXT_SETUP
87 | 57 | eWORD_100MPS | eTEXT_SOAK
88 | 58 | eWORD_1000MPS | eTEXT_STARTUP
89 | 59 | eWORD_STEP
90 | 5A | eWORD_SWITCH_CONTROL_LOOP_OFF
91 | 5B | eWORD_TEST_SOURCE_SYSTEM
92 | 5C | eWORD_SWITCH_TO_MANUAL_CONTROL
93 | 5D | eWORD_SOURCE_EVENT_19 | eTEXT_T
94 | 5E | eWORD_TENTHS | eTEXT_TENTHS
95 | 5F | eWORD_LIGHT_ON_OFF | eTEXT_THERMOCOUPLE
96 | 60 | eWORD_THOUSANDTHS
97 | 61 | eWORD_SOURCE_EVENT_25 | eTEXT_ALARM_HYSTERESIS
98 | 62 | eWORD_SOURCE_EVENT_24 | eTEXT_TUNE
99 | 63 | eWORD_SOURCE_DIN27 | eTEXT_UNDER
100 | 64 | eWORD_USER
101 | 65 | eWORD_SOURCE_CLP7_ALARM | eTEXT_USER_SET_1
102 | 66 | eWORD_SOURCE_CLP6_ALARM | eTEXT_USER_SET_2
103 | 67 | eWORD_VARIABLE_TIME_BASE | eTEXT_VARIABLE_TIME_BASE
104 | 68 | eWORD_VOLTS | eTEXT_VOLTS
105 | 69 | eWORD_WHOLE | eTEXT_WHOLE
106 | 6A | eWORD_YES | eTEXT_YES
107 | 6B | eWORD_SOURCE_CLP5_ALARM | eTEXT_IDLE
108 | 6C | eWORD_SOURCE_CLP4_ALARM | eTEXT_SILENCE
109 | 6D | eWORD_ACTION_REQUEST
110 | 6E | eWORD_LIMIT_SOURCE_AIN1 | eTEXT_OPEN_SET_POINT
111 | 6F | eWORD_LIMIT_SOURCE_AIN3 | eTEXT_TEST_SOURCE_COMMS
112 | 70 | eWORD_MILLIAMPS | eTEXT_MILLIAMPS
113 | 71 | eWORD_RTD_100_OHM | eTEXT_RTD_100_OHM
114 | 72 | eWORD_DOOR | eTEXT_RTD_1000_OHM
115 | 73 | eWORD_DOOR_OPEN | eTEXT_RTD_500_OHM
116 | 74 | eWORD_TRIGGER_OUTPUT | eTEXT_JUMP_LOOP
117 | 75 | eWORD_SOURCE_AIN3 | eTEXT_PROFILE_08_STEP_X
118 | 76 | eWORD_SOURCE_EVENT_47 | eTEXT_TIMEOUT
119 | 77 | eWORD_SOURCE_DEV_ALARM | eTEXT_WAITING_FOR_CROSS_1_POS
120 | 78 | eWORD_SOURCE_EVENT_20 | eTEXT_WAITING_FOR_CROSS_1_NEG
121 | 79 | eWORD_SOURCE_EVENT_21 | eTEXT_WAITING_FOR_CROSS_2_POS
122 | 7A | eWORD_SOURCE_EVENT_22 | eTEXT_WAITING_FOR_CROSS_2_NEG
123 | 7B | eWORD_SOURCE_EVENT_23 | eTEXT_WAITING_FOR_CROSS_3_POS
124 | 7C | eWORD_SOURCE_EVENT_46 | eTEXT_HALF_WAVE
125 | 7D | eWORD_SOURCE_EVENT_45 | eTEXT_INTERMITTENT
126 | 7E | eWORD_SOURCE_EVENT_44 | eTEXT_LIMIT
127 | 7F | eWORD_SOURCE_EVENT_43 | eTEXT_SHORTED
128 | 80 | eWORD_ANALOG_OUTPUT_1 | eTEXT_SYNCHRONIZED_VARIABLE_TIME_BASE
129 | 81 | eWORD_ANALOG_OUTPUT_2 | eTEXT_CLEAR
130 | 82 | eWORD_ANALOG_OUTPUT_3 | eTEXT_INPUT_ERROR_1_MESSAGE
131 | 83 | eWORD_ANALOG_OUTPUT_7 | eTEXT_INPUT_ERROR_2_MESSAGE
132 | 84 | eWORD_ANALOG_OUTPUT_8 | eTEXT_ALARM_1_MESSAGE
133 | 85 | eWORD_ANALOG_OUTPUT_9 | eTEXT_ALARM_2_MESSAGE
134 | 86 | eWORD_ANALOG_OUTPUT_13 | eTEXT_LIMIT_1_MESSAGE
135 | 87 | eWORD_ANALOG_OUTPUT_14 | eTEXT_TUNING_1_MESSAGE
136 | 88 | eWORD_ANALOG_OUTPUT_15 | eTEXT_RAMPING_1_MESSAGE
137 | 89 | eWORD_ANALOG_OUTPUT_19 | eTEXT_DEVICE_ERROR_MESSAGE
138 | 8A | eWORD_ANALOG_OUTPUT_20 | eTEXT_OK
139 | 8B | eWORD_ANALOG_OUTPUT_21 | eTEXT_BAD_CAL_DATA
140 | 8C | eWORD_PROCESS_OUTPUT_1 | eTEXT_MEASUREMENT_ERROR
141 | 8D | eWORD_PROCESS_OUTPUT_3 | eTEXT_RTD_ERROR
142 | 8E | eWORD_PROCESS_OUTPUT_5 | eTEXT_ANALOG_INPUT
143 | 8F | eWORD_TIME | eTEXT_TIME
144 | 90 | eWORD_PROCESS_OUTPUT_7 | eTEXT_WAIT_EVENT
145 | 91 | eWORD_SOURCE_AIN3_LIGHT | eTEXT_PROFILE_09_STEP_X
146 | 92 | eWORD_SOURCE_EVENT_42 | eTEXT_PAUSE
147 | 93 | eWORD_SOURCE_EVENT_41 | eTEXT_RESUME
148 | 94 | eWORD_SOURCE_EVENT_40 | eTEXT_TERMINATE
149 | 95 | eWORD_RUNNING | eTEXT_RUNNING
150 | 96 | eWORD_SOURCE_ALL_LIGHTS_OFF | eTEXT_WAITING_FOR_CROSS_3_NEG
151 | 97 | eWORD_SOURCE_ANY_LIGHT_ON | eTEXT_MEASURING_MAX_PEAK
152 | 98 | eWORD_SOURCE_CLP2_ALARM | eTEXT_MEASURING_MIN_PEAK
153 | 99 | eWORD_SOURCE_CLP3_ALARM | eTEXT_CALCULATING
154 | 9A | eWORD_SOURCE_EVENT_39 | eTEXT_CAL_IN_OFFSET
155 | 9B | eWORD_SOURCE_EVENT_38 | eTEXT_1K_POT
156 | 9C | eWORD_DISPLAY_UNITS | eTEXT_DISPLAY_UNITS
157 | 9D | eWORD_SOURCE_EVENT_37 | eTEXT_ADDRESS
158 | 9E | eWORD_AUTOTUNE | eTEXT_AUTOTUNE
159 | 9F | eWORD_CONTROL_LOOP | eTEXT_USER_CONTROL_MODE
160 | A0 | eWORD_CHA_POWER | eTEXT_HEAT_POWER
161 | A1 | eWORD_CHB_POWER | eTEXT_COOL_POWER
162 | A2 | eWORD_INTEGRAL | eTEXT_INTEGRAL
163 | A3 | eWORD_DERIVATIVE | eTEXT_DERIVATIVE
164 | A4 | eWORD_DEADBAND | eTEXT_DEADBAND
165 | A5 | eWORD_SOURCE_EVENT_36 | eTEXT_HEAT_ALGORITHM
166 | A6 | eWORD_SOURCE_EVENT_35 | eTEXT_HEAT_PROPBAND
167 | A7 | eWORD_SOURCE_EVENT_34 | eTEXT_ON_OFF_HEAT_HYSTERESIS
168 | A8 | eWORD_SOURCE_EVENT_33 | eTEXT_COOL_ALGORITHM
169 | A9 | eWORD_SOURCE_EVENT_32 | eTEXT_COOL_PROPBAND
170 | AA | eWORD_SOURCE_EVENT_31 | eTEXT_ON_OFF_COOL_HYSTERESIS
171 | AB | eWORD_CHA_P_TERM | eTEXT_HEAT_PROPORTIONAL_TERM
172 | AC | eWORD_CHA_I_TERM | eTEXT_HEAT_INTEGRAL_TERM
173 | AD | eWORD_CHA_D_TERM | eTEXT_HEAT_DERIVATIVE_TERM
174 | AE | eWORD_CHB_P_TERM | eTEXT_COOL_PROPORTIONAL_TERM
175 | AF | eWORD_CHB_I_TERM | eTEXT_COOL_INTEGRAL_TERM
176 | B0 | eWORD_CHB_D_TERM | eTEXT_COOL_DERIVATIVE_TERM
177 | B1 | eWORD_SETUP_ETHERNET | eTEXT_RAMP_RATE
178 | B2 | eWORD_SETUP_GLOBAL | eTEXT_SSR_FAULT
179 | B3 | eWORD_SETUP_DIAGNOSTICS | eTEXT_SENSED_CURRENT
180 | B4 | eWORD_SOURCE_EVENT_30 | eTEXT_CUSTOM
181 | B5 | eWORD_SOURCE_EVENT_29 | eTEXT_LIMIT_SET_POINT_LOW
182 | B6 | eWORD_SOURCE_EVENT_28 | eTEXT_LIMIT_SET_POINT_HIGH
183 | B7 | eWORD_SOURCE_EVENT_27 | eTEXT_LIMIT_HYSTERESIS
184 | B8 | eWORD_SOURCE_EVENT_26 | eTEXT_HEATER_FAULT
185 | B9 | eWORD_SOURCE_SP3 | eTEXT_PROFILE_10_STEP_X
186 | BA | eWORD_SOURCE_SP3_LIGHT | eTEXT_PROFILE_11_STEP_X
187 | BB | eWORD_SOURCE_DIN1 | eTEXT_PROFILE_12_STEP_X
188 | BC | eWORD_9600_BAUD | eTEXT_9600
189 | BD | eWORD_19200_BAUD | eTEXT_19200
190 | BE | eWORD_38400_BAUD | eTEXT_38400
191 | BF | eWORD_SOURCE_DIN26 | eTEXT_EVEN
192 | C0 | eWORD_SOURCE_DIN25 | eTEXT_ODD
193 | C1 | eWORD_SOURCE_DIN24 | eTEXT_INPUT_VOLTAGE
194 | C2 | eWORD_SOURCE_DIN2 | eTEXT_PROFILE_02_STEP_X
195 | C3 | eWORD_SOURCE_DIN3 | eTEXT_PROFILE_03_STEP_X
196 | C4 | eWORD_SOURCE_DIN23 | eTEXT_START_PROFILE_NUMBER
197 | C5 | eWORD_SOURCE_DIN22 | eTEXT_RUI
198 | C6 | eWORD_SOURCE_DIN21 | eTEXT_HOME_UPPER
199 | C7 | eWORD_SOURCE_DIN20 | eTEXT_HOME_LOWER
200 | C8 | eWORD_CLOUD_PORT_UNSECURE | eTEXT_READ_SECURITY
201 | C9 | eWORD_CLOUD_PORT_SECURE | eTEXT_WRITE_SECURITY
202 | CA | eWORD_SOURCE_DIN19 | eTEXT_DISPLAY_INTENSITY
203 | CB | eWORD_SOURCE_DIN18 | eTEXT_ACTION_PROMPT
204 | CC | eWORD_SOURCE_DIN17 | eTEXT_IGNORE
205 | CD | eWORD_SOURCE_DIN16 | eTEXT_TRU_TUNE_ENABLE
206 | CE | eWORD_SOURCE_DIN15 | eTEXT_PROFILE_DISABLE
207 | CF | eWORD_SOURCE_DIN14 | eTEXT_PROFILE_HOLD_RESUME
208 | D0 | eWORD_SOURCE_DIN13 | eTEXT_PROFILE_START_STOP
209 | D1 | eWORD_SOURCE_DIN12 | eTEXT_WAIT_PROCESS
210 | D2 | eWORD_SOURCE_DIN11 | eTEXT_WAIT_BOTH
211 | D3 | eWORD_SOURCE_DIN10 | eTEXT_DASHES
212 | D4 | eWORD_SOURCE_DIN9 | eTEXT_DUPLEX
213 | D5 | eWORD_ANALOG_OUTPUT | eTEXT_RETRANSMIT
214 | D6 | eWORD_SOURCE_DIN8 | eTEXT_OUTPUT_CURVE1
215 | D7 | eWORD_SOURCE_DIN7 | eTEXT_OUTPUT_CURVE2
216 | D8 | eWORD_SOURCE_DIN6 | eTEXT_REMOTE_SP_ENABLE
217 | D9 | eWORD_SOURCE_DIN5 | eTEXT_LOCK_KEYPAD
218 | DA | eWORD_SOURCE_DIN4 | eTEXT_FORCE_ALARM
219 | DB | eWORD_SOURCE_SP7 | eTEXT_TRU_TUNE_DISABLE
220 | DC | eWORD_LOGGED_IN | eTEXT_ALL_LOOP_ALARM_OFF
221 | DD | eWORD_LOGIN_SUCCESSFUL | eTEXT_OPEN_LOOP_ERROR
222 | DE | eWORD_LOGIN_FAILED | eTEXT_UNLOCK
223 | DF | eWORD_LOGGED_OUT | eTEXT_INPUT_ERROR
224 | E0 | eWORD_LOGIN_DISABLED | eTEXT_ALARM_ERROR
225 | E1 | eWORD_SECURITY_LEVEL_4 | eTEXT_LIMIT_ERROR
226 | E2 | eWORD_SECURITY_LEVEL_3 | eTEXT_MODBUS_ADDRESS
227 | E3 | eWORD_SECURITY_LEVEL_2 | eTEXT_LOAD_USER_SET
228 | E4 | eWORD_SECURITY_LEVEL_1 | eTEXT_LOCK
229 | E5 | eWORD_LIGHT_DIM | eTEXT_THERMISTOR
230 | E6 | eWORD_COMPLIMENTARY | eTEXT_COMPARE
231 | E7 | eWORD_SOURCE_AIN7 | eTEXT_COUNTER
232 | E8 | eWORD_SOURCE_EVENT_1 | eTEXT_UNUSED_01
233 | E9 | eWORD_SOURCE_EVENT_2 | eTEXT_PROFILE_EVENT_A
234 | EA | eWORD_SOURCE_EVENT_3 | eTEXT_PROFILE_EVENT_B
235 | EB | eWORD_SOURCE_EVENT_4 | eTEXT_PROFILE_EVENT_C
236 | EC | eWORD_SOURCE_EVENT_5 | eTEXT_PROFILE_EVENT_D
237 | ED | eWORD_SOURCE_EVENT_6 | eTEXT_UNUSED_02
238 | EE | eWORD_SOURCE_SP6 | eTEXT_LINEARIZATION
239 | EF | eWORD_LOGIC | eTEXT_LOGIC
240 | F0 | eWORD_SOURCE_AIN6 | eTEXT_MATH
241 | F1 | eWORD_SOURCE_PV | eTEXT_PV
242 | F2 | eWORD_SOURCE_SP | eTEXT_SET_POINT_CLOSED
243 | F3 | eWORD_SOURCE_SP5 | eTEXT_SET_POINT_OPEN
244 | F4 | eWORD_SOURCE_AIN5 | eTEXT_TIMER
245 | F5 | eWORD_SOURCE_SP4 | eTEXT_VARIABLE
246 | F6 | eWORD_SOURCE_AIN4 | eTEXT_NOT_SOURCED
247 | F7 | eWORD_SOURCE_EVENT_7 | eTEXT_PROFILE_EVENT_E
248 | F8 | eWORD_SOURCE_EVENT_8 | eTEXT_PROFILE_EVENT_F
249 | F9 | eWORD_SOURCE_EVENT_9 | eTEXT_PROFILE_EVENT_G
250 | FA | eWORD_SOURCE_EVENT_10 | eTEXT_PROFILE_EVENT_H
eEND_WATBUS_TEXT
251 | eTEXT_PROFILE_EVENT_H,
252 | // Percival Specific parameter text
253 | eTEXT_PLANT_GROWTH,
254 | eTEXT_INCUBATOR,
255 | eEND_OF_ENUMERATED_PARAMETER_TEXT,